## Instrument Index
Tag No | Supplied By | Manufacturer | Model | Calibration Certificate | ATEX Certificate | Manual | Calibration Range Low | Calibration Range High | Calibration Range UOM | Location Drawing | Install Detail Dwg Number | Loop/Interconnection/Schematic Dwg No | PID No | Datasheet No | I/O Type | IS/Non-IS I/O | Hazardous Area Classification | External Power | Remarks
F1.S1.DS.CDS01.CMA001-TE103A | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0116 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA001-TIT103A | PJ002 | SIEMENS | SITRANS TH300 | E363404-PJ002-130-006-0039_Calibration-TIT103A |  |  | 0 | 110 | DEG C | H363404-00000-270-272-0007 | H363404-00000-270-260-0007 | H363404-00000-270-262-0025-0001 | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0116 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA001-TE103C | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0118 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA001-TIT103C | PJ002 | SIEMENS | SITRANS TH300 | E363404-PJ002-130-006-0039_Calibration-TIT103C |  |  | 0 | 110 | DEG C | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | H363404-00000-270-262-0002-0002 | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0118 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA001-FE105 | PJ002 | SIEMENS | MAG3100 | E363404-PJ002-130-006-0039_Calibration-FE105-FIT105 | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0051 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA001-FIT105 | PJ002 | SIEMENS | MAG6000I | E363404-PJ002-130-006-0039_Calibration-FE105-FIT105 | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 561.6 | M3/H | H363404-00000-270-272-0007 | H363404-00000-270-260-0005 | H363404-00000-270-262-0025-0001 | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0051 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.CDS01.CMA001-PIT112 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-260-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0002-0002 | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0001 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA001-PIT127 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 660 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0003 | H363404-00000-270-262-0025-0002 | H363404-CDS01-270-276-0001 | H363404-PJ002-270-206-0002 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA003-TE203 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0119 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA003-TIT203 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 109 | DEG C | H363404-00000-270-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0026-0001 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0119 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.GPB003-PIT221 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 660 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0026-0001 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0007 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA003-PIT222 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0003 | H363404-00000-270-262-0026-0001 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0003 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.GPA001-PIT226 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1920 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0003 | H363404-00000-270-262-0026-0002 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0008 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA003-FE227 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0053 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.CMA003-FIT227 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 3 | M3/H | H363404-00000-260-272-0007 | H363404-00000-270-260-0006 | H363404-00000-270-262-0026-0002 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0053 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.CDS01.GPA001-DIT228 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2500 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0029-0001 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0054 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.GPA001-FE228 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0054 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.GPA001-FIT228 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 2.9 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0026-0002 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0054 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.CDS01.CMA003-PDIT230 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 44 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0004 | H363404-00000-270-262-0026-0002 | H363404-CDS01-270-276-0002 | H363404-PJ002-270-206-0004 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-FE110 | PJ002 | SIEMENS | SITRANS FM MAG3100 | E363404-PJ002-130-006-0039_Calibration-FE110 | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0052 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-FIT110 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.36 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0005 | H363404-00000-270-262-0027-0002 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0052 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.CDS01.EGC001-FE209 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0055 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-FIT209 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 66.26 | M3/H | H363404-00000-260-272-0005 | H363404-00000-270-260-0005 | H363404-00000-270-262-0027-0002 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0055 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.CDS01.EGC001-TE209 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0120 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-TIT209 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 110 | DEG C | H363404-00000-270-272-0007 | H363404-00000-270-260-0007 | H363404-00000-270-262-0027-0002 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0120 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-PIT217A | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 660 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0027-0002 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0009 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-PIT217B | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 660 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0028-0001 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0169 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-FE220 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0057 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-FIT220 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.37 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0005 | H363404-00000-270-262-0028-0001 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0057 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.CDS01.EGC001-TE225 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0122 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-TIT225 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 54 | DEG C | H363404-00000-260-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0028-0001 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0122 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.CDS01.EGC001-PDIT251 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 69 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0004 | H363404-00000-270-262-0028-0002 | H363404-CDS01-270-276-0003 | H363404-PJ002-270-206-0146 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.GPB001-DIT116 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2000 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0079-0001 | H363404-EFT01-270-276-0001 | H363404-PJ002-270-206-0058 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.GPB001-FE116 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-EFT01-270-276-0001 | H363404-PJ002-270-206-0058 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.GPB001-FIT116 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 19.26 | M3/H | H363404-00000-270-272-0004 | H363404-00000-270-260-0006 | H363404-00000-270-262-0073-0001 | H363404-EFT01-270-276-0001 | H363404-PJ002-270-206-0058 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.EFT01.CMA001-TE125 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-EFT01-270-276-0001 | H363404-PJ002-270-206-0123 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.CMA001-TIT125 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 96 | DEG C | H363404-00000-270-272-0004 | H363404-00000-270-260-0007 | H363404-00000-270-262-0073-0001 | H363404-EFT01-270-276-0001 | H363404-PJ002-270-206-0123 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.CMA001-FE130 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-EFT01-270-276-0001 | H363404-PJ002-270-206-0147 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.CMA001-FIT130 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.072 | M3/H | H363404-00000-270-272-0004 | H363404-00000-270-260-0005 | H363404-00000-270-262-0073-0002 | H363404-EFT01-270-276-0001 | H363404-PJ002-270-206-0147 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.EFT01.CMA002-FE117 | PJ002 | SIEMENS | SITRANS MASS2100 |  | E363404-PJ002-130-006-0036_ATEX-MASS2100 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0059 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.CMA002-FIT117 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 0.12 | M3/H | H363404-00000-270-272-0004 | H363404-00000-270-260-0005 | H363404-00000-270-262-0074-0001 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0059 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.EFT01.HQ001-FE118 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0060 | N/A | NIS | N/A | -
F1.S1.DS.EFT01.HQ001-FIT118 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 8.64 | M3/H | H363404-00000-270-272-0002 | H363404-00000-270-260-0006 | H363404-00000-270-262-0097-0001 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0060 | AI | NIS | N/A | 24 VDC
F1.S1.DS.EFT01.CMA002-TE119 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0124 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.CMA002-TIT119 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 74 | DEG C | H363404-00000-270-272-0004 | H363404-00000-270-260-0007 | H363404-00000-270-262-0074-0001 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0124 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.GPA003-PIT121 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1200 | KPA (G) | H363404-00000-270-272-0004 | H363404-00000-270-260-0003 | H363404-00000-270-262-0074-0002 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0010 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.GPA003-FE122 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0061 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.GPA003-FIT122 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 25 | M3/H | H363404-00000-270-272-0004 | H363404-00000-270-260-0005 | H363404-00000-270-262-0074-0002 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0061 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.EFT01.HQ001-FE127 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0062 | N/A | NIS | N/A | -
F1.S1.DS.EFT01.HQ001-FIT127 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 10 | M3/H | H363404-00000-270-272-0001 | H363404-00000-270-260-0005 | H363404-00000-270-262-0097-0001 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0062 | AI | NIS | N/A | 24 VDC
F1.S1.DS.EFT01.HQ001-PIT128 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1730 | KPA (G) | H363404-00000-270-272-0002 | H363404-00000-270-260-0003 | H363404-00000-270-262-0097-0001 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0148 | AI | NIS | N/A | -
F1.S1.DS.EFT01.HQ001-PIT135 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1200 | KPA (G) | H363404-00000-270-272-0001 | H363404-00000-270-260-0003 | H363404-00000-270-262-0097-0002 | H363404-EFT01-270-276-0002 | H363404-PJ002-270-206-0168 | AI | NIS | N/A | -
F1.S1.DS.EFT01.GPA005-FE212 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-EFT01-270-276-0003 | H363404-PJ002-270-206-0063 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.EFT01.GPA005-FIT212 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1.33 | M3/H | H363404-00000-270-272-0004 | H363404-00000-270-260-0005 | H363404-00000-270-262-0073-0002 | H363404-EFT01-270-276-0003 | H363404-PJ002-270-206-0063 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.FPH01.GPB002-DIT511 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2500 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0079-0002 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0067 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.GPB002-FE511 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0067 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.GPB002-FIT511 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 52.8 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0075-0001 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0067 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.FPH01.CMA001-FE515 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0064 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.CMA001-FIT515 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 2.5 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0075-0001 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0064 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.FPH01.CMA002-FE516 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0065 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.CMA002-FIT516 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 2.5 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0075-0001 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0065 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.FPH01.GPB002-PIT517 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 770 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0003 | H363404-00000-270-262-0075-0001 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0011 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.GPB001-DIT518 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2500 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0079-0002 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0066 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.GPB001-FE518 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0066 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.GPB001-FIT518 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 52.8 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0075-0002 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0066 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.FPH01.GPB001-TE520 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0125 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.FPH01.GPB002-TIT520 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 59 | DEG C | H363404-00000-270-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0075-0002 | H363404-FPH01-270-276-0001 | H363404-PJ002-270-206-0125 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.IXS01.HSA003-FIT453 | PM024 | ABB | TBD |  |  |  | 3.6 | 180 | M3/H | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | 24 VDC | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV454 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV455 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV456 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV457 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV458 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV459 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV460 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV461 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV462 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV463 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV464 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV465 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV466 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XV469 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY454 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY455 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY456 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY457 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY458 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY459 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY460 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY461 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY462 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY463 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY464 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY465 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY466 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-XY469 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC454 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC455 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC456 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC457 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC458 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC459 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC460 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC461 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC462 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC463 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC464 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC465 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC466 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSC469 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO454 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO455 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO456 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO457 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO458 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO459 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO460 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO461 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO462 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO463 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO464 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO465 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO466 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-ZSO469 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-FE473 | PM024 | ABB | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | N/A | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-FIT473 | PM024 | ABB | TBD |  |  |  | 3.6 | 180 | M3/H | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | 24 VDC | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-PIT471 | PM024 | ABB | TBD |  |  |  | 0 | 2400 | KPA (G) | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-PIT472 | PM024 | ABB | TBD |  |  |  | 0 | 2400 | KPA (G) | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV474 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV475 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV476 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV477 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV478 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV479 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV480 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV481 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV482 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV483 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV484 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV485 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV486 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XV489 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY474 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY475 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY476 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY477 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY478 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY479 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY480 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY481 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY482 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY483 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY484 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY485 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY486 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-XY489 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC474 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC475 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC476 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC477 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC478 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC479 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC480 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC481 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC482 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC483 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC484 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC485 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC486 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSC489 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO474 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO475 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO476 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO477 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO478 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO479 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO480 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO481 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO482 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO483 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO484 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO485 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO486 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA004-ZSO489 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | E363404-PM024-210-276-0001 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.EGC001-TE101 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-IXS01-270-276-0001 | H363404-PJ002-270-206-0126 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.EGC001-TE102 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-IXS01-270-276-0001 | H363404-PJ002-270-206-0150 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.EGC001-TIT101 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 60 | DEG C | H363404-00000-270-272-0001 | H363404-00000-270-260-0007 | H363404-00000-270-262-0100-0002 | H363404-IXS01-270-276-0001 | H363404-PJ002-270-206-0126 | AI | NIS | N/A | -
F1.S1.DS.IXS01.EGC001-TIT102 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 60 | DEG C | H363404-00000-270-272-0001 | H363404-00000-270-260-0007 | H363404-00000-270-262-0100-0002 | H363404-IXS01-270-276-0001 | H363404-PJ002-270-206-0150 | AI | NIS | N/A | -
F1.S1.DS.IXS01.CMA001-FE215 | PJ002 | SIEMENS | SITRANS MASS2100 |  | E363404-PJ002-130-006-0036_ATEX-MASS2100 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0070 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.IXS01.CMA001-FE216 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0071 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.IXS01.CMA001-FIT215 | PJ002 | SIEMENS | SITRANS FCT010/30 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 0.0024 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0049-0001 | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0070 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.IXS01.CMA001-FIT216 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.29 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0049-0001 | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0071 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.IXS01.CMA001-TE218 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0127 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.IXS01.CMA001-TIT218 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 60 | DEG C | H363404-00000-270-272-0003 | H363404-00000-270-260-0007 | H363404-00000-270-262-0049-0002 | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0127 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.IXS01.GPB001-FE221 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0072 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.GPB001-FIT221 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 22.82 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0049-0002 | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0072 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.GPB001-PIT220 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 580 | KPA (G) | H363404-00000-270-272-0003 | H363404-00000-270-260-0003 | H363404-00000-270-262-0049-0002 | H363404-IXS01-270-276-0002 | H363404-PJ002-270-206-0012 | AI | NIS | N/A | -
F1.S1.DS.IXS01.CMA003-FE326 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0073 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA003-FE327 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0074 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA003-FIT326 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1.21 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0098-0002 | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0073 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.CMA003-FIT327 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 8.6 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0006 | H363404-00000-270-262-0101-0001 | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0074 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.CMA003-TE317 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0128 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA003-TIT317 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 68 | DEG C | H363404-00000-270-272-0003 | H363404-00000-270-260-0007 | H363404-00000-270-262-0101-0001 | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0128 | AI | NIS | N/A | -
F1.S1.DS.IXS01.GPB005-DIT318 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2500 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0106-0002 | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0075 | AI | NIS | N/A | -
F1.S1.DS.IXS01.GPB005-FE318 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0075 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.GPB005-FIT318 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 24.97 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0098-0001 | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0075 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.GPB005-PIT319 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 640 | KPA (G) | H363404-00000-270-272-0003 | H363404-00000-270-260-0003 | H363404-00000-270-262-0098-0001 | H363404-IXS01-270-276-0003 | H363404-PJ002-270-206-0013 | AI | NIS | N/A | -
F1.S1.DS.IXS01.GPA007-FE418 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-IXS01-270-276-0004 | H363404-PJ002-270-206-0076 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.GPA007-FIT418 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1.5 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0098-0002 | H363404-IXS01-270-276-0004 | H363404-PJ002-270-206-0076 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.GPA007-PIT419 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1812 | KPA (G) | H363404-00000-270-272-0003 | H363404-00000-270-260-0003 | H363404-00000-270-262-0099-0001 | H363404-IXS01-270-276-0004 | H363404-PJ002-270-206-0014 | AI | NIS | N/A | -
F1.S1.DS.IXS01.HSA001-FO401 | PJ002 | SIEMENS | AccuO4-71S-2G-C-6-A1-88-B??-D0-16S-Z C52+Y40+Y99 |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0002 |  | N/A | H363404-IXS01-270-276-0004 | H363404-PJ002-270-206-0165 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.HSA002-FE433 | PM024 | ABB | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | N/A | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-FIT433 | PM024 | ABB | TBD |  |  |  | 3.6 | 180 | M3/H | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | 24 VDC | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-PIT431 | PM024 | ABB | TBD |  |  |  | 0 | 2400 | KPA (G) | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-PIT432 | PM024 | ABB | TBD |  |  |  | 0 | 2400 | KPA (G) | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV434 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV435 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV436 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV437 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV438 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV439 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV440 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV441 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV442 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV443 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV444 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV445 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV446 | PM024 | FLO-TITE/MAXSEAL / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XV449 | PM024 | FLO-TITE / ROTORK | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY434 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY435 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY436 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY437 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY438 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY439 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY440 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY441 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY442 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY443 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY444 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY445 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY446 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-XY449 | PM024 | LUCIFER | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC434 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC435 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC436 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC437 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC438 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC439 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC440 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC441 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC442 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC443 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC444 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC445 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC446 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSC449 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO434 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO435 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO436 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO437 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO438 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO439 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO440 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO441 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO442 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO443 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO444 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO445 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO446 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA002-ZSO449 | PM024 | IFM | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-FE453 | PM024 | ABB | TBD |  |  |  | N/A | N/A | N/A | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | N/A | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-PIT451 | PM024 | ABB | TBD |  |  |  | 0 | 2400 | KPA (G) | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.HSA003-PIT452 | PM024 | ABB | TBD |  |  |  | 0 | 2400 | KPA (G) | E363404-PM024-250-250-0001 | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | H363404-IXS01-270-276-0004 |  | SOFT | NIS | N/A | - | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.IXS01.CMA005-FE601 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0077 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA005-FE603 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0078 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA005-FIT601 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.96 | M3/H | H363404-00000-270-272-0002 | H363404-00000-270-260-0005 | H363404-00000-270-262-0099-0002 | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0077 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.CMA005-FIT603 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 14.4 | M3/H | H363404-00000-270-272-0002 | H363404-00000-270-260-0006 | H363404-00000-270-262-0100-0001 | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0078 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.CMA005-TE605 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0129 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA005-TIT605 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 49 | DEG C | H363404-00000-270-272-0002 | H363404-00000-270-260-0007 | H363404-00000-270-262-0100-0001 | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0129 | AI | NIS | N/A | -
F1.S1.DS.IXS01.GPB009-FE608 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0079 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.GPB009-FIT608 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 59.04 | M3/H | H363404-00000-270-272-0002 | H363404-00000-270-260-0005 | H363404-00000-270-262-0100-0001 | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0079 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.GPB009-PIT610 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 540 | KPA (G) | H363404-00000-270-272-0002 | H363404-00000-270-260-0003 | H363404-00000-270-262-0100-0002 | H363404-IXS01-270-276-0005 | H363404-PJ002-270-206-0015 | AI | NIS | N/A | -
F1.S1.DS.PLI01.GPB008-FE418 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-PLI01-270-276-0005 | H363404-PJ002-270-206-0098 | N/A | NIS | N/A | -
F1.S1.DS.PLI01.GPB008-FIT418 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 24 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0101-0001 | H363404-PLI01-270-276-0005 | H363404-PJ002-270-206-0098 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.CMA002-FE322 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0110 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA002-FIT322 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 6.4 | M3/H | H363404-00000-270-272-0002 | H363404-00000-270-260-0006 | H363404-00000-270-262-0099-0002 | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0110 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.CMA002-FO330 | PJ002 | SIEMENS | AccuO4-71S-1F-C-6-A1-88-B??-D0-16S-Z C52+Y40+Y99 |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0002 |  | N/A | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0170 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.CMA002-FO331 | PJ002 | SIEMENS | AccuO4-71S-1F-C-6-A1-88-B??-D0-16S-Z C52+Y40+Y99 |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0002 |  | N/A | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0171 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.GPB003-FE320 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 114 | M3/H | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | H363404-00000-270-262-0099-0001 | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0111 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.GPB003-FIT320 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 114 | M3/H | H363404-00000-270-272-0002 | H363404-00000-270-260-0006 | H363404-00000-270-262-0099-0001 | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0111 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01.HSA001.UCA01 | PM024 | [5 empty] | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | E363404-PM024-260-260-0001 | N/A | N/A | N/A | NIS | N/A | 230 VAC | PM024 HOLD PENDING VENDOR INFORMATION ON INSTRUMENT MAKE AND MODEL
F1.S1.DS.NDS01.CMA001-FE101 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0080 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA001-FIT101 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1440 | M3/H | H363404-00000-270-272-0007 | H363404-00000-270-260-0005 | H363404-00000-270-262-0001-0001 | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0080 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.NDS01.CMA001-TE103A | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0130 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA001-TIT103A | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 110 | DEG C | H363404-00000-270-272-0007 | H363404-00000-270-260-0007 | H363404-00000-270-262-0002-0001 | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0130 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA001-TE103C | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0132 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA001-TIT103C | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 110 | DEG C | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | H363404-00000-270-262-0004-0001 | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0132 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA001-PIT117 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-260-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0003-0002 | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0016 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA001-PIT127 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 760 | KPA (G) | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0003 | H363404-00000-270-262-0001-0002 | H363404-NDS01-270-276-0001 | H363404-PJ002-270-206-0017 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA002-FE107 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0082 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA002-FIT107 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1440 | M3/H | H363404-00000-270-272-0007 | H363404-00000-270-260-0005 | H363404-00000-270-262-0001-0001 | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0082 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.NDS01.CMA002-TE109A | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0133 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA002-TIT109A | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 110 | DEG C | H363404-00000-270-272-0007 | H363404-00000-270-260-0007 | H363404-00000-270-262-0002-0001 | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0133 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA002-TE109C | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0135 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA002-TIT109C | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 110 | DEG C | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | H363404-00000-270-262-0004-0001 | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0135 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA002-PIT118 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-260-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0003-0002 | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0018 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA002-PIT227 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 760 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0003 | H363404-00000-270-262-0002-0001 | H363404-NDS01-270-276-0002 | H363404-PJ002-270-206-0019 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.GPB001-DIT205 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2500 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0005-0001 | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0084 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.GPB001-FE205 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0084 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.GPB001-FIT205 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 19 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0004-0002 | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0084 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.NDS01.CMA004-TE206 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0136 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA004-TIT206 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 109 | DEG C | H363404-00000-270-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0004-0002 | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0136 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.GPB001-PIT223 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 260 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0003 | H363404-00000-270-262-0004-0002 | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0022 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA004-FE225 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0083 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.CMA004-FIT225 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 17.2 | M3/H | H363404-00000-260-272-0007 | H363404-00000-270-260-0005 | H363404-00000-270-262-0004-0002 | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0083 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.NDS01.CMA004-PIT226 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-260-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0005-0001 | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0021 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.GPB001-PDIT230 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 41 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0004 | H363404-00000-270-262-0005-0001 | H363404-NDS01-270-276-0003 | H363404-PJ002-270-206-0020 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.GPB003-PIT222 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 760 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0006-0002 | H363404-NDS01-270-276-0004 | H363404-PJ002-270-206-0026 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.EGC001-FE117 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0081 | N/A | NIS | N/A | -
F1.S1.DS.NDS01.EGC001-FIT117 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 2.35 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0005 | H363404-00000-270-262-0006-0001 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0081 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.NDS01.EGC001-TE215 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0137 | N/A | NIS | N/A | -
F1.S1.DS.NDS01.EGC001-TIT215 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 110 | DEG C | H363404-00000-270-272-0007 | H363404-00000-270-260-0007 | H363404-00000-270-262-0006-0001 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0137 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.EGC001-FE216 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0085 | N/A | NIS | N/A | -
F1.S1.DS.NDS01.EGC001-FIT216 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 2.4 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0005 | H363404-00000-270-262-0006-0001 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0085 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.NDS01.EGC001-FE224 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0087 | N/A | NIS | N/A | -
F1.S1.DS.NDS01.EGC001-FIT224 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 426 | M3/H | H363404-00000-270-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0006-0002 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0087 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.NDS01.EGC001-TE225 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0139 | N/A | NIS | N/A | -
F1.S1.DS.NDS01.EGC001-TIT225 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 54 | DEG C | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | H363404-00000-270-262-0006-0002 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0139 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.EGC001-PIT245A | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 756 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0007-0001 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0152 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.EGC001-PIT245B | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 756 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0003 | H363404-00000-270-262-0007-0001 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0153 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.EGC001-PDIT247 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 51 | KPA (G) | H363404-00000-270-272-0007 | H363404-00000-270-260-0004 | H363404-00000-270-262-0007-0001 | H363404-NDS01-270-276-0005 | H363404-PJ002-270-206-0151 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.NDS01.XM01-PI401 | PJ002 | SIEMENS | SITRANS TF field indicator |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0103-0001 | H363404-RUS01-270-276-0004 | H363404-PJ002-270-206-0043 | N/A | NIS | N/A | -
F1.S1.DS.NDS01.XM01-PIT401 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1140 | KPA (G) | H363404-00000-270-272-0010 | H363404-00000-270-260-0003 | H363404-00000-270-262-0103-0001 | H363404-RUS01-270-276-0004 | H363404-PJ002-270-206-0043 | AI | NIS | N/A | -
F1.S1.DS.OGT01.HSB001-TE203 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0140 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.HSB001-TIT203 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 60 | DEG C | H363404-00000-270-272-0006 | H363404-00000-270-260-0007 | H363404-00000-270-262-0076-0001 | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0140 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.HSB001-PIT204 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-270-272-0006 | H363404-00000-270-260-0003 | H363404-00000-270-262-0076-0001 | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0027 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.GQB001-TE212 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0141 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.GQB001-TIT212 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 72 | DEG C | H363404-00000-270-272-0006 | H363404-00000-270-260-0007 | H363404-00000-270-262-0077-0001 | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0141 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.GQB001-PIT213 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-270-272-0006 | H363404-00000-270-260-0003 | H363404-00000-270-262-0077-0001 | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0028 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.CMA001-FE218 | PJ002 | SIEMENS | SITRANS MASS2100 |  | E363404-PJ002-130-006-0036_ATEX-MASS2100 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0088 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.CMA001-FIT218 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 0.24 | M3/H | H363404-00000-270-272-0007 | H363404-00000-270-260-0006 | H363404-00000-270-262-0076-0001 | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0088 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.OGT01.HSB001-FE220 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0089 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.OGT01.HSB001-FIT220 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 4.8 | M3/H | H363404-00000-260-272-0005 | H363404-00000-270-260-0006 | H363404-00000-270-262-0076-0002 | H363404-OGT01-270-276-0002 | H363404-PJ002-270-206-0089 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.CMA001-TE102 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0143 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA001-TIT102 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 109 | DEG C | H363404-00000-270-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0050-0001 | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0143 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.GPB001-DIT110 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2500 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0056-0001 | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0091 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.GPB001-FE110 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0091 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.GPB001-FIT110 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 23 | M3/H | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | H363404-00000-270-262-0050-0001 | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0091 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.GPB001-PIT123 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 170 | KPA (G) | H363404-00000-270-272-0005 | H363404-00000-270-260-0003 | H363404-00000-270-262-0050-0002 | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0030 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA002-TE126 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0144 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA002-TIT126 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 109 | DEG C | H363404-00000-270-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0050-0002 | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0144 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA001-FE128 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0090 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA001-FIT128 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1.11 | M3/H | H363404-00000-260-272-0007 | H363404-00000-270-260-0005 | H363404-00000-270-262-0050-0002 | H363404-PLI01-270-276-0001 | H363404-PJ002-270-206-0090 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.CMA003-FE121 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0002 | H363404-PJ002-270-206-0092 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA003-FIT121 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.19 | M3/H | H363404-00000-270-272-0008 | H363404-00000-270-260-0005 | H363404-00000-270-262-0051-0001 | H363404-PLI01-270-276-0002 | H363404-PJ002-270-206-0092 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.GPB003-PIT122 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 570 | KPA (G) | H363404-00000-270-272-0004 | H363404-00000-270-260-0003 | H363404-00000-270-262-0051-0002 | H363404-PLI01-270-276-0002 | H363404-PJ002-270-206-0032 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA003-PIT124 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | -30 | 0 | KPA (G) | H363404-00000-270-272-0008 | H363404-00000-270-260-0003 | H363404-00000-270-262-0051-0002 | H363404-PLI01-270-276-0002 | H363404-PJ002-270-206-0031 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.GPB003-FIT224 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 36 | M3/H | H363404-00000-270-272-0004 | H363404-00000-270-260-0006 | H363404-00000-270-262-0051-0002 | H363404-PLI01-270-276-0002 | H363404-PJ002-270-206-0154 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.GPB003-DIT224 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 3000 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0056-0002 | H363404-PLI01-270-276-0002 | H363404-PJ002-270-206-0154 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.GPB003-FE224 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0002 |  | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA004-FE221 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0003 | H363404-PJ002-270-206-0093 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA004-FIT221 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.19 | M3/H | H363404-00000-270-272-0008 | H363404-00000-270-260-0005 | H363404-00000-270-262-0053-0001 | H363404-PLI01-270-276-0003 | H363404-PJ002-270-206-0093 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.GPB006-PIT316 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1050 | KPA (G) | H363404-00000-270-272-0003 | H363404-00000-270-260-0003 | H363404-00000-270-262-0053-0001 | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0033 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA006-FE324 | PJ002 | SIEMENS | SITRANS MASS2100 |  | E363404-PJ002-130-006-0036_ATEX-MASS2100 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0094 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA006-FIT324 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 0.0081 | M3/H | H363404-00000-270-272-0008 | H363404-00000-270-260-0006 | H363404-00000-270-262-0052-0002 | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0094 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.GPB006-FE325 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0097 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.GPB006-FIT325 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 24 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0053-0002 | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0097 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.CMA007-FE329 | PJ002 | SIEMENS | SITRANS MASS2100 |  | E363404-PJ002-130-006-0036_ATEX-MASS2100 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0095 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA007-FIT329 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 0.0081 | M3/H | H363404-00000-270-272-0008 | H363404-00000-270-260-0006 | H363404-00000-270-262-0052-0002 | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0095 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.CMA008-FIT330 | PJ002 | SIEMENS | SITRANS MASS2100 |  | E363404-PJ002-130-006-0036_ATEX-MASS2100 |  | 0 | 0.0081 | M3/H | H363404-00000-270-272-0008 | H363404-00000-270-260-0006 | H363404-00000-270-262-0053-0002 | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0096 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.CMA008-FE330 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-PLI01-270-276-0004 | H363404-PJ002-270-206-0096 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.HQ001-PIT416 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 960 | KPA (G) | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS |  | H363404-00000-270-262-0102-0001 | H363404-PLI01-270-276-0005 | H363404-PJ002-270-206-0158 | AI | NIS | N/A | -
F1.S1.DS.PLI01.HQ001-FE417 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-PLI01-270-276-0005 | H363404-PJ002-270-206-0155 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.HQ001-FIT417 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 14.4 | M3/H | H363404-00000-270-272-0008 | H363404-00000-270-260-0006 | H363404-00000-270-262-0054-0001 | H363404-PLI01-270-276-0005 | H363404-PJ002-270-206-0155 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.GPB008-PIT420 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 310 | KPA (G) | H363404-00000-270-272-0003 | H363404-00000-270-260-0003 | H363404-00000-270-262-0101-0002 | H363404-PLI01-270-276-0005 | H363404-PJ002-270-206-0035 | AI | NIS | N/A | -
F1.S1.DS.PLI01.GPB010-DIT411 | PJ002 | SIEMENS | PART OF FIT |  |  |  | 0 | 2000 | KG/M3 | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | VENDOR PRE-INSTALLED | H363404-00000-270-262-0120-0001 | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0099 | AI | NIS | N/A | -
F1.S1.DS.PLI01.GPB010-FE411 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0099 | N/A | NIS | N/A | -
F1.S1.DS.PLI01.GPB010-FIT411 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 19.58 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0006 | H363404-00000-270-262-0102-0001 | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0099 | AI | NIS | N/A | 24 VDC
F1.S1.DS.PLI01.GPB010-PIT421 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 340 | KPA (G) | H363404-00000-270-272-0003 | H363404-00000-270-260-0003 | H363404-00000-270-262-0102-0002 | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0036 | AI | NIS | N/A | -
F1.S1.DS.PLI01.CMA009-FE601 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0156 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.PLI01.CMA009-FIT601 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 11.35 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0006 | H363404-00000-270-262-0054-0001 | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0156 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.PLI01.GPB010-FE604 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 19.58 | M3/H | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | H363404-00000-270-262-0102-0002 | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0157 | AI | NIS | N/A | 24 VDC
F1.S1.DS.PLI01.GPB010-FIT604 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 19.58 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0102-0002 | H363404-PLI01-270-276-0006 | H363404-PJ002-270-206-0157 | AI | NIS | N/A | 24 VDC
F1.S1.DS.IXS01 PLI01.GPB003-FIT320 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0111 | N/A | NIS | N/A | -
F1.S1.DS.IXS01.GPB003-FE320 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0111 | N/A | NIS | N/A | -
F1.S1.DS.RRS01.CMA001-FE102 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0100 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.CMA001-FIT102 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1.53 | M3/H | H363404-00000-270-272-0001 | H363404-00000-270-260-0005 | H363404-00000-270-262-0054-0001 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0100 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.RRS01.CMA001-FE103 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0101 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.CMA001-FIT103 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.39 | M3/H | H363404-00000-270-272-0001 | H363404-00000-270-260-0005 | H363404-00000-270-262-0054-0001 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0101 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.RRS01.CMA001-FE117 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0102 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.CMA001-FIT117 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 7.2 | M3/H | H363404-00000-270-272-0001 | H363404-00000-270-260-0006 | H363404-00000-270-262-0054-0002 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0102 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.RRS01.GPA001-PIT119 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 840 | KPA (G) | H363404-00000-270-272-0001 | H363404-00000-270-260-0003 | H363404-00000-270-262-0054-0002 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0038 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.GPA001-FE122 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0104 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.GPA001-FIT122 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 25 | M3/H | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | H363404-00000-270-262-0054-0002 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0104 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.RRS01.GPA001-FE123 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0105 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.GPA001-FIT123 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 10 | M3/H | H363404-00000-270-272-0001 | H363404-00000-270-260-0005 | H363404-00000-270-262-0097-0002 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0105 | AI | NIS | N/A | 24 VDC
F1.S1.DS.RRS01.CMA001-TE123 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0145 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.CMA001-TIT123 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 | 109 | DEG C | H363404-00000-270-272-0001 | H363404-00000-270-260-0007 | H363404-00000-270-262-0055-0001 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0145 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.CMA001-FE124 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0103 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RRS01.CMA001-FIT124 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1.91 | M3/H | H363404-00000-270-272-0001 | H363404-00000-270-260-0005 | H363404-00000-270-262-0054-0002 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0103 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.RRS01.GPA001-PIT135 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 840 | KPA (G) | H363404-00000-270-272-0001 | H363404-00000-270-260-0003 | H363404-00000-270-262-0098-0001 | H363404-RRS01-270-276-0001 | H363404-PJ002-270-206-0159 | AI | NIS | N/A | -
F1.S1.DS.RRS01.HQ001-FE116 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-RRS01-270-276-0002 | H363404-PJ002-270-206-0107 | N/A | NIS | N/A | -
F1.S1.DS.RRS01.HQ001-FIT116 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 8.64 | M3/H | H363404-00000-270-272-0001 | H363404-00000-270-260-0006 | H363404-00000-270-262-0097-0002 | H363404-RRS01-270-276-0002 | H363404-PJ002-270-206-0107 | AI | NIS | N/A | 24 VDC
F1.S1.DS.RRS01.GPA003-FE121 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | N/A | H363404-RRS01-270-276-0002 | H363404-PJ002-270-206-0106 | N/A | NIS | N/A | -
F1.S1.DS.RRS01.GPA003-FIT121 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 0.19 | M3/H | H363404-00000-270-272-0003 | H363404-00000-270-260-0005 | H363404-00000-270-262-0101-0002 | H363404-RRS01-270-276-0002 | H363404-PJ002-270-206-0106 | AI | NIS | N/A | 24 VDC
F1.S1.DS.RRS01.HQ001-PIT122 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 840 | KPA (G) | H363404-00000-270-272-0001 | H363404-00000-270-260-0003 | H363404-00000-270-262-0102-0001 | H363404-RRS01-270-276-0002 | H363404-PJ002-270-206-0039 | AI | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-PIT101 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 910 | KPA (G) | H363404-00000-270-272-0010 | H363404-00000-270-260-0003 | H363404-00000-270-262-0102-0002 | H363404-RUS01-270-276-0001 | H363404-PJ002-270-206-0040 | AI | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-FE102 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0001 | H363404-PJ002-270-206-0108 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-FIT102 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 1.8 | M3/H | H363404-00000-270-272-0010
F1.S1.DS.RUS01.XM01-PI201 | PJ002 | SIEMENS | SITRANS TF field indicator |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0103-0001 | H363404-RUS01-270-276-0002 | H363404-PJ002-270-206-0041 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.XM01-PIT201 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1440 | KPA (G) | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0103-0001 | H363404-RUS01-270-276-0002 | H363404-PJ002-270-206-0041 | AI | NIS | N/A | -
F1.S1.DS.RUS01.XM01-FE202 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0002 | H363404-PJ002-270-206-0109 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.XM01-FIT202 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 49.2 | M3/H | H363404-00000-270-272-0010 | H363404-00000-270-260-0005 | H363404-00000-270-262-0103-0001 | H363404-RUS01-270-276-0002 | H363404-PJ002-270-206-0109 | AI | NIS | N/A | 24 VDC
F1.S1.DS.RUS01.XM01-FIT325 | PJ002 | SIEMENS | SITRANS FCT030 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | 0 | 4.8 | M3/H | H363404-00000-270-272-0007 | H363404-00000-270-260-0006 | H363404-00000-270-262-0078-0002 | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0112 | AI | IS | II 3 G - Ex i IIC T1 | 24 VDC
F1.S1.DS.RUS01.XM01-FE325 | PJ002 | SIEMENS | SITRANS FCS300 |  | E363404-PJ002-130-006-0036_ATEX-FCS300-FCT030 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0006 | N/A | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0112 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.IXS01.GPB003-PIT326 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1200 | KPA (G) | H363404-00000-270-272-0002 |  | H363404-00000-270-262-0100-0002 | H363404-RUS01-270-276-0003 | H363404-PJ002-270-206-0162 | AI | NIS | N/A | -
F1.S1.DS.RUS01.XM01-PI501 | PJ002 | SIEMENS | SITRANS TF field indicator |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0005 |  | H363404-00000-270-262-0075-0002 | H363404-RUS01-270-276-0005 | H363404-PJ002-270-206-0044 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.XM01-PIT501 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1920 | KPA (G) | H363404-00000-270-272-0005 | Note: Minimum of 1.5 m of impulse tubing to be installed in order to reduce temperature of measured medium. 2 tees, 2 unions, drain valve, and plug also needed. | H363404-00000-270-262-0075-0002 | H363404-RUS01-270-276-0005 | H363404-PJ002-270-206-0044 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.XM01-FE504 | PJ002 | SIEMENS | SITRANS FX330 |  | E363404-PJ002-130-006-0036_ATEX-FX330 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS |  | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0005 | H363404-PJ002-270-206-0113 | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.XM01-FIT504 | PJ002 | SIEMENS | PART OF F1.S1.DS.RUS01.XM01_FE504 |  |  |  | 0 | 4.8 | T/H | H363404-00000-270-272-0005 |  | H363404-00000-270-262-0075-0002 | H363404-RUS01-270-276-0005 | H363404-PJ002-270-206-0113 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.GPB121-PI601 | PJ002 | SIEMENS | SITRANS TF field indicator |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0103-0002 | H363404-RUS01-270-276-0006 | H363404-PJ002-270-206-0047 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-PIT601 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1800 | KPA (G) | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0103-0002 | H363404-RUS01-270-276-0006 | H363404-PJ002-270-206-0047 | AI | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-FE602 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0006 | H363404-PJ002-270-206-0114 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-FIT602 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 2.7 | M3/H | H363404-00000-270-272-0010 | H363404-00000-270-260-0005 | H363404-00000-270-262-0103-0002 | H363404-RUS01-270-276-0006 | H363404-PJ002-270-206-0114 | AI | NIS | N/A | 24 VDC
F1.S1.DS.RUS01.GPB121-PIT608 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1800 | KPA (G) | H363404-00000-270-272-0004 | H363404-00000-270-260-0003 | H363404-00000-270-262-0073-0002 | H363404-RUS01-270-276-0006 | H363404-PJ002-270-206-0163 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.GPB121-PIT701 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1860 | KPA (G) | H363404-00000-270-272-0010 | H363404-00000-270-260-0003 | H363404-00000-270-262-0103-0002 | H363404-RUS01-270-276-0007 | H363404-PJ002-270-206-0048 | AI | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-FE702 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0007 | H363404-PJ002-270-206-0115 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.GPB121-FIT702 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | 0 | 5.3 | M3/H | H363404-00000-270-272-0010 | H363404-00000-270-260-0005 | H363404-00000-270-262-0103-0002 | H363404-RUS01-270-276-0007 | H363404-PJ002-270-206-0115 | AI | NIS | N/A | 24 VDC
F1.S1.DS.RUS01.GPB121-PIT703 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 1860 | KPA (G) | H363404-00000-270-272-0010 | H363404-00000-270-260-0003 | H363404-00000-270-262-0104-0001 | H363404-RUS01-270-276-0007 | H363404-PJ002-270-206-0164 | AI | NIS | N/A | -
F1.S1.DS.RUS01.XM01-PI806 | PJ002 | SIEMENS | SITRANS TF field indicator |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0104-0001 | H363404-RUS01-270-276-0008 | H363404-PJ002-270-206-0049 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.XM01-PIT806 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 840 | KPA (G) | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0104-0001 | H363404-RUS01-270-276-0008 | H363404-PJ002-270-206-0049 | AI | NIS | N/A | -
F1.S1.DS.RUS01.XM01-PI902 | PJ002 | SIEMENS | SITRANS TF field indicator |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0104-0001 | H363404-RUS01-270-276-0009 | H363404-PJ002-270-206-0050 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.XM01-PIT902 | PJ002 | SIEMENS | SITRANS P320 |  | E363404-PJ002-130-006-0036_ATEX-P320 |  | 0 | 840 | KPA (G) | H363404-00000-270-272-0010 |  | H363404-00000-270-262-0104-0001 | H363404-RUS01-270-276-0009 | H363404-PJ002-270-206-0050 | AI | NIS | N/A | -
F1.S1.DS.RUS01.XM01-FO907 | PJ002 | SIEMENS | AccuO4-71S-89S-C-6-A1-88-B??-D0-16S-Z C52+Y40+Y99 |  |  |  | N/A | N/A | N/A | H363404-00000-270-272-0001 |  | N/A | H363404-RUS01-270-276-0009 | H363404-PJ002-270-206-0161 | N/A | NIS | N/A | -
F1.S1.DS.RUS01.EGC03-TE816 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0012 |  | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.EGC03-TIT816 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 |  | DEG C | H363404-00000-270-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0079-0001 | H363404-RUS01-270-276-0012 | H363404-PJ002-270-206-0166 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.EGC03-TE817 | PJ002 | SIEMENS | SITRANS TS500 | N/F | E363404-PJ002-130-006-0036_ATEX-TS500 |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0007 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0012 |  | N/A | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.EGC03-TIT817 | PJ002 | SIEMENS | SITRANS TH300 |  |  |  | 0 |  | DEG C | H363404-00000-270-272-0005 | H363404-00000-270-260-0007 | H363404-00000-270-262-0079-0001 | H363404-RUS01-270-276-0012 | H363404-PJ002-270-206-0167 | AI | IS | II 3 G - Ex i IIC T1 | -
F1.S1.DS.RUS01.EGC03-FE818 | PJ002 | SIEMENS | SITRANS FM MAG3100 |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  | N/A | N/A | N/A | FIELD DETERMINED BASED ON THE 3D MODEL, P&IDS, AND PIPING ISOMETRICS | H363404-00000-270-260-0005 | REFER TO MANUFACTURER'S STANDARD/MANUAL | H363404-RUS01-270-276-0012 | H363404-PJ002-270-206-0172 | N/A |  |  | -
F1.S1.DS.RUS01.EGC03-FIT818 | PJ002 | SIEMENS | SITRANS FM MAG6000I |  | E363404-PJ002-130-006-0036_ATEX-MAG3100-MAG6000I |  |  |  |  | H363404-00000-270-272-0005 | H363404-00000-270-260-0005 | H363404-00000-270-262-0079-0001 | H363404-RUS01-270-276-0012 | H363404-PJ002-270-206-0172 | AI |  |  | -